## Slide 1
WOMBAT Tutorial
NAWEA WindTech
Rob Hammond
2 November 2023

## Slide 2
WOMBAT At a Glance
Configuring WOMBAT
COREWIND Assumptions
Setting Up a Simulation
Hands-on With WOMBAT
Time Permitting: WAVES
Time Permitting: Future of WOMBAT

## Slide 3
WOMBAT At a Glance

## Slide 4: Relevance of O&M Costs
O&M activities are estimated to comprise between 29% and 34% of total wind plant lifecycle costs (Stehly & Beiter, 2018).
  $33 – $59/kW/year for land-based wind
  $65 – $194/kw/year for offshore wind
Innovations in the O&M sector have the potential to drive down the overall cost of wind energy.
However, quantifying the impact of these innovations on cost is challenging because:
  Data on wind plant O&M costs are not often publicly available or broken down into detailed categories.
  Understanding cost impacts and tradeoffs for O&M strategies requires a model with appropriate resolution to capture relatively small changes at the level of individual tasks.

## Slide 5: Primary Research Question
How might maintenance strategies, technological innovations, and site conditions influence wind plant OpEx and ultimately LCOE?
Methodology Innovations
Technology Innovations
Site Conditions
Notes: How do different O&M strategies, technological and methodological innovations, and site-specific conditions impact the overall OpEx costs, and in turn LCOE, for a given land-based or offshore windfarm?

## Slide 6: Approach
Minimal code by the user to actual run the model
  Empower a broad user base by requiring minimal Python skills
  Configure models through YAML files, not complicated setup code
Prescriptive modeling via discrete event simulation:
  Enables weather and site-specific variability
  Allows a user to define O&M strategies to understand cost and energy impacts
  Focuses on what-if scenario modeling instead of optimization
Modular and flexible code base:
  Allows for new methodologies to be tested with ease
  Provides a tool to analyze both offshore and land-based windfarm O&M costs
  Allows users to define their turbine failure models in as much or as little detail as desired
Documentation driven development:
  Use of inline comments and docstrings explains what nearly all functionality is supposed to be doing
  Enables easier modification or improvement for researchers and/or developers

## Slide 7: High-Level Software Architecture
Wind Farm Model
Turbines
Substations
Repair Manager
Servicing Equipment
Core Model
Cables
Electrical System
Electronic Control
Rotor Blades
Drivetrain
Gearbox
Generator
Sensors
Mechanical Brake
Hydraulic System
Supporting Structure
Rotor Hub
Yaw System
Transformer
Cable
Systems
Example Subassemblies
Environment
Port
Data Classes
Simulation API
Post Processing

## Slide 8: High-Level Simulation Architecture
Model evaluates O&M costs using discrete event simulation (series of events in sequential order where no changes occur between events):
  Allows for detailed documentation of a system and its processes.
  Allows for a prescriptive approach for exploring specific impacts compared to an optimization with a “best choice.”
Start simulation
End simulation
Wind (and wave) time series
Subassembly
Fails or reaches maintenance interval
System
Requests service
Repair Manager
Assigns task
Servicing Equipment
Conducts service
System
Returns to operation
Accumulate downtime (failures only)
Track O&M costs
Wait for weather, equipment, parts*
*Parts availability not yet implemented
Subassembly
Resets status

## Slide 9
Configuring WOMBAT

## Slide 10: Repairs and Maintenance
Maintenance (scheduled)
  Fixed frequency model (number of days) to align with regular servicing intervals
Failures (unscheduled maintenance)
  Weibull distribution (exponential if using 1 for the shape parameter)
    Scale = 1 / (# Failures/system/year) = MTBF (in years)
  Random sampling for the next time a failure occurs
Shared parameterizations
  Materials cost (whole cost or proportional to system CapEx)
  Repair time
  Service equipment categories that can perform corrective maintenance
    CTV, DRN, RMT, SCN, LCN, CAB, DSV, TOW, AHV
  Operating reduction
  Severity level (helps prioritize repairs across the farm)

## Slide 11: Servicing Equipment
Strategy
  Scheduled
  Unscheduled-downtime
  Unscheduled-requests
  Unscheduled-tow (offshore only)
Capabilities
Working hours
Mobilization
Port distance
Crew
Weather constraints
  Windspeed
  Waveheight
  Speed (including during inclement weather)
  Non-operational periods
  Slow down periods

## Slide 12: The Wind Farm
CSV Layout
Define each substation and turbine’s positions relative to each other and spatially (WGS-84 coordinates)
Provides pointers to the cable, substation, and turbine definition file
Gives names and IDs to each of the systems on the farm so that subassembly definitions can be shared between common systems

## Slide 13: Baseline Inputs
Subassemblies
Failure rate(s)
Maintenance tasks
Equipment requirements
Cost and time to complete repairs
Power curve (if modeling energy production – IEC power curve)
Servicing Equipment
Maintenance strategy and related definitions
Port (if required)
Capabilities
Labor rates
Equipment rates
Operational limits
Miscellaneous
Weather profile
  Hourly windspeed and/or wave height
Windfarm layout
Site working hours
Port distance

## Slide 14: Outputs
Time-based availability
Production-based availability
Power production
Fixed costs
Capacity factor
Task completion rate
Service equipment costs
Service equipment utilization
Labor costs
Combined service equipment and labor costs by productivity
Component costs
Servicing time breakdown
OpEx
More on the way
High fidelity log files to compute further metrics
Event logs
Operating level logs (hourly)
Power production logs (hourly)
Power potential logs (hourly)

## Slide 15: Examples

## Slide 16
COREWIND Assumptions

## Slide 17: High Level Information
Plant assumptions https://corewind.eu/wp-content/uploads/files/publications/COREWIND-D6.1-General-frame-of-the-analysis-and-description-of-the-new-FOW-assessment-app.pdf
Assessment assumptions https://corewind.eu/wp-content/uploads/files/publications/COREWIND-D4.2-Floating-Wind-O-and-M-Strategies-Assessment.pdf
Summary
1.2 GW in Morro Bay, CA with reference coordinate: (35. 367222, -121. 645163)
60km distance to shore
80 x IEA 15 MW Reference Turbines, but with floating platforms, spaced 2160m apart
2 offshore substations
7 CTVs, Anchor Handling Vessel, Diving Support Vessel, Cable Lay Vessel, ROV
Technician salary: €80K

## Slide 18: Plant Layout
Notes: failure rates primarily from ECN tool and prior IEA Wind work
crane costs and sizes from LandBOSSE, vessel data from ORBIT

## Slide 19: Failure Data
Component or Maintenance Task | Frequency (scheduled) | Failure Rate (N/turbine/year) | Duration (hours) | Technicians (number) | Cost (Euros) | Vessel
Sub-Sea Inspections of Cables, Mooring Lines and Floater Hull | 2 years |  | 12 | 5 | 500 | SOV with ROV
Direct Drive Generator – Minor Failure |  | 0.546 | 13 | 2 | 1000 | CTV
Main Shaft – Replacement |  | 0.009 | 144 | 5 | 232000 | CTV
Data doesn’t quite match the expected format in WOMBAT
Some assumptions don’t quite align with expectations
So, how would this get translated to WOMBAT given what we know?

## Slide 20: Vessel Data
Vessel | Number | Purpose | Dayrate (Euros) | Mobilization Cost (Euros) | Waveheight Limit (m)
Crew Transfer Vessel (CTV) | 7 | Access to systems | 3,500 | 0 | 2 (simplified from matrix)
Anchor Handling Vessel (AHV) | 1 | Mooring line and anchor repairs | 55,000 | 500,000 | 2.5
SOV with ROV | 2 | Subsea inspection and repairs | 75,000 | 225,000 | 2
Monohull Crane Vessel (HLV) | 1 | Major component exchange offshore | 290,000 | 325,000 | 2
Tugboat | 2 | Tow-in and tow-out | 30,000 | 200,000 | 2.5
Data doesn’t quite match the expected format in WOMBAT
Some assumptions don’t quite align with expectations
So, how would this get translated to WOMBAT given what we know?

## Slide 21
Setting Up a Simulation

## Slide 22: Working Through the Simulation Setup
We will work through creating a piece of every simulation aspect in this part of the workshop from the layout to servicing equipment
Focus on understanding how to get each of the aspects set up and how everything interconnects, not exhaustively recreating the paper’s assumptions
To run the model, ask new questions of the scenarios, generally tinker, we’ll then switch to what is already available on the GitHub repository

## Slide 23: Create a New Project
Note: everything we need is already set up in the repository
Open a VSCode (or preferred code editor/IDE) window
In the terminal/Anaconda prompt
  “cd <your-path-the-workshop-data>”
  “python”
  “from wombat import create_library_structure”
  “create_library_structure(<your-library-name>)”

## Slide 24: Overarching configuration file
Create a configuration file in <library>/project/config called “base.yaml”
Now, we need to create most of the inputs on the right as direct inputs or pointers to other files: https://wisdem.github.io/WOMBAT/API/simulation_api.html#configuration
To get started, I’ll directly guide this first part

## Slide 25: Overarching configuration file - Answer

## Slide 26: Layout
Create a layout CSV file in <library>/project/plant/ using the file name you used for “layout” in base.yaml
Open it in Excel, Numbers, or whatever you prefer for editing tabular data
Add the columns you see to the right: https://wisdem.github.io/WOMBAT/examples/how_to.html#windfarm-layout
Create the first string for each substation with the information that we have (fill in optional pieces as you please)—layout on Slide 17
NOTE: “subassembly” and “upstream_cable” just need the file names

## Slide 27: Layout - Answer
4 strings per substation, plus a connections between them and the interconnection point (unmodeled)
Zero-indexing is required for string/order

## Slide 28: Servicing Equipment
7 CTVs, 1 Anchor Handling Vessels, 2 SOVs with ROV, 1 Heavy Lift Vessel, 2 Tugboats
Modifications needed: No SOVs (yet) in WOMBAT, so we will model 2 ROVs
2 classes of vessels: scheduled and unscheduled, so how would we classify the vessels in the first bullet?
https://wisdem.github.io/WOMBAT/API/types.html#scheduled-service-equipment
https://wisdem.github.io/WOMBAT/API/types.html#unscheduled-service-equipment

## Slide 29: Scheduled Servicing Equipment
D4.2, p. 18
Create a YAML configuration file in “<library>/vessels/”, for a single CTV.
https://wisdem.github.io/WOMBAT/API/types.html#scheduled-service-equipment

## Slide 30: Scheduled Servicing Equipment - Answer

## Slide 31: Unscheduled Servicing Equipment
D4.2, p. 18
Create a YAML configuration file in “<library>/vessels/”, for an HLV and tugboat.
https://wisdem.github.io/WOMBAT/API/types.html#unscheduled-service-equipment

## Slide 32: Unscheduled Servicing Equipment - Answer

## Slide 33: Substations
D4.2, p13-17
Create a YAML file in <library>/substations/ using the file name you used in “subassembly” for your layout file
Create the maintenance and failure configurations for the OSS
https://wisdem.github.io/WOMBAT/examples/how_to.html#substations

## Slide 34: Substations
Left: Maintenance
https://wisdem.github.io/WOMBAT/API/types.html#maintenance-tasks
Right: Failure
https://wisdem.github.io/WOMBAT/API/types.html#failures

## Slide 35: Substations - Answer

## Slide 36: Turbines
D4.2, p13-17
Create a YAML file in <library>/turbines/ using the file name you used in “subassembly” for your layout file
What subassemblies should we consider for the turbine model?
Create the maintenance and failure configurations for the hydraulic system (ballast pump and pitch system)
Right: https://wisdem.github.io/WOMBAT/examples/how_to.html#turbines

## Slide 37: Turbines - Answer

## Slide 38: Cables
D4.2, p13-17
Create a YAML file in <library>/cables/ using the file name you used in “upstream_cable” for your layout file
Create the maintenance and failure configurations for the export cables
Right: https://wisdem.github.io/WOMBAT/examples/how_to.html#cables

## Slide 39: Cables - Answer

## Slide 40
Hands-on With WOMBAT

## Slide 41: Running a Simulation
Final questions on setup before moving forward?
From the terminal, launch a Jupyter Lab session: “jupyter lab”
I’ll switch over the example notebook that’s setup to finish out the workshop

## Slide 42
WAVES
Combining ORBIT, WOMBAT, and FLORIS in a single model
Notes: Leave 15 minutes for this so we can get ample feedback from DOE for their perspective on what should be built out
Can be posed as a question to DOE also

## Slide 43: WAVES
Release coming soon at: https://github.com/NREL/WAVES
Combine CapEx (ORBIT), OpEx (WOMBAT), and AEP (FLORIS) into a single model API that creates the required input and output connections to properly consider project financials and real world energy production (availability and wakes)

## Slide 44
Future of WOMBAT
What’s on the horizon for WOMBAT over the next few years?
Notes: Leave 15 minutes for this so we can get ample feedback from DOE for their perspective on what should be built out
Can be posed as a question to DOE also

## Slide 45: Potential Future Work
Model tow-to-port simulations at a higher resolution.
Improved repair timing.
Date-based maintenance.
Single file/dictionary configuration similar to ORBIT and FLORIS.
Multi-crew handoff.
Other ideas? Add them to the Issues board: https://github.com/WISDEM/WOMBAT/issues
Floating Wind model comparison publication in 2024 to update the state of O&M modeling.
Develop a baseline land-based, fixed offshore, and floating offshore wind data set for easier modeling.
Model Development
Validation and Review

## Slide 46
Thank you
This work was authored by the National Renewable Energy Laboratory, operated by Alliance for Sustainable Energy, LLC, for the U.S. Department of Energy (DOE) under Contract No. DE-AC36-08GO28308. Funding provided by the U.S. Department of Energy Office of Energy Efficiency and Renewable Energy Wind Energy Technologies Office. The views expressed in the article do not necessarily represent the views of the DOE or the U.S. Government. The U.S. Government retains and the publisher, by accepting the article for publication, acknowledges that the U.S. Government retains a nonexclusive, paid-up, irrevocable, worldwide license to publish or reproduce the published form of this work, or allow others to do so, for U.S. Government purposes.
Notes: Revised November 13, 2019 – Elizabeth/Bill