## LBW
Baseline case - land-based wind
Wind farm parameters
79 turbines
1 substation
Array cables: 33 kV
Wind turbine parameters
Capacity: 2.6 MW
Capex: $850/kW
power_curve: 2019COE_Market_Average_2.6MW_121.csv |  | https://github.com/NREL/turbine-models/blob/master/Onshore/2019COE_Market_Average_2.6MW_121.csv
Maintenance inputs
annual service: 60 hours, CTV, $20,000
Failure and repair inputs
System | Subassembly Name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Severity Level
Turbine | electrical_system | minor repair | 2.414 | 1 | 5 | 113 | CTV | 0 | 1
Turbine | electrical_system | major repair | 54 | 1 | 14 | 2260 | CTV | 0 | 2
Turbine | electrical_system | major replacement | 432 | 1 | 18 | 14690 | CTV | 1 | 3
Turbine | electrical_system | relay minor repair | 2.725 | 1 | 4 | 294 | CTV | 0 | 1
Turbine | electrical_system | relay major repair | 16.45 | 1 | 19 | 2599 | CTV | 0 | 2
Turbine | electrical_system | relay major replacement | 444 | 1 | 150 | 15255 | CTV | 1 | 3
Turbine | electrical_system | power supply minor repair | 11.84 | 1 | 7 | 271 | CTV | 0 | 1
Turbine | electrical_system | power supply major repair | 11.1 | 1 | 14 | 5989 | CTV | 0 | 2
Turbine | electrical_system | power supply major replacement | 180 | 1 | 57 | 14690 | CTV | 1 | 3
Turbine | electronic_control | minor repair | 2.7 | 1 | 8 | 226 | CTV | 0 | 1
Turbine | electronic_control | major repair | 17.7 | 1 | 14 | 2260 | CTV | 0 | 2
Turbine | electronic_control | major replacement | 958 | 1 | 12 | 14690 | CTV | 1 | 3
Turbine | sensors | minor repair | 3.7 | 1 | 8 | 170 | CTV | 0 | 1
Turbine | sensors | major repair | 13.1 | 1 | 6 | 2825 | CTV | 0 | 2
Turbine | hydraulic_system | minor pitch system repair | 1.132 | 1 | 9 | 237 | CTV | 0 | 1
Turbine | hydraulic_system | major pitch system repair | 5.2 | 1 | 19 | 2147 | CTV | 0 | 2
Turbine | hydraulic_system | major pitch system replacement | 933 | 1 | 25 | 15820 | CTV | 1 | 3
Turbine | hydraulic_system | minor pump motor repair | 3.337 | 1 | 4 | 373 | CTV | 0 | 1
Turbine | hydraulic_system | major pump motor repair | 21.6 | 1 | 10 | 2260 | CTV | 0 | 2
Turbine | yaw_system | minor repair | 5.5 | 1 | 5 | 158 | CTV | 0 | 1
Turbine | yaw_system | major repair | 149 | 1 | 20 | 3390 | CTV | 0.3 | 2
Turbine | yaw_system | major replacement | 894 | 1 | 49 | 14125 | CTV | 1 | 3
Turbine | rotor_blades | minor repair | 1.969 | 1 | 9 | 192 | CTV | 0 | 1
Turbine | rotor_blades | major repair | 89.8 | 1 | 21 | 1695 | CTV | 0 | 2
Turbine | rotor_blades | major replacement | 898 | 1 | 288 | 101700 | LCN | 1 | 3
Turbine | mechanical_brake | other minor repair | 1.048 | 1 | 5 | 124 | CTV | 0 | 1
Turbine | mechanical_brake | other major repair | 20.3 | 1 | 21 | 2712 | CTV | 0 | 2
Turbine | mechanical_brake | other major replacement | 851 | 1 | 36 | 11300 | CTV | 0 | 3
Turbine | rotor_hub | n/a | 5.167 | 1 | 10 | 181 | CTV | 0 | 1
Turbine | rotor_hub | major repair | 24.7 | 1 | 40 | 1695 | CTV | 0 | 2
Turbine | rotor_hub | major replacement | 940 | 1 | 298 | 107350 | CTV | 1 | 3
Turbine | gearbox | minor repair | 2.348 | 1 | 8 | 141 | CTV | 0 | 1
Turbine | gearbox | major repair | 24.4 | 1 | 22 | 2825 | CTV | 0 | 2
Turbine | gearbox | major replacement | 6.022 | 1 | 231 | 259900 | LCN | 1 | 3
Turbine | generator | minor repair | 1.86 | 1 | 7 | 181 | CTV | 0 | 1
Turbine | generator | major repair | 2.8 | 1 | 24 | 3955 | CTV | 0 | 2
Turbine | generator | major replacement | 9.494 | 1 | 81 | 67800 | LCN | 1 | 3
Turbine | supporting_structure | minor repair | 10.6 | 1 | 5 | 158 | CTV | 0 | 1
Turbine | supporting_structure | major repair | 11 | 1 | 2 | 1243 | CTV | 0 | 2
Turbine | supporting_structure | minor safety repair | 2.578 | 1 | 2 | 147 | CTV | 0 | 1
Turbine | supporting_structure | major safety repair | 240 | 1 | 7 | 2712 | CTV | 0 | 2
Turbine | supporting_structure | minor service item repair | 8.1 | 1 | 7 | 90 | CTV | 0 | 1
Turbine | supporting_structure | major service item repair | 872 | 1 | 14 | 1356 | CTV | 0 | 2
Turbine | supporting_structure | minor HVAC repair | 4.868 | 1 | 5 | 525 | CTV | 0 | 1
Turbine | supporting_structure | major HVAC repair | 132 | 1 | 14 | 1469 | CTV | 0 | 2
Turbine | drive_train | minor oil/grease repair | 2.154 | 1 | 4 | 181 | CTV | 0 | 1
Turbine | drive_train | major oil/grease repair | 146 | 1 | 18 | 2260 | CTV | 0 | 2
Substaion | transformer | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
Substaion | transformer | major repair | 287 | 1 | 26 | 2599 | CTV | 0 | 2
Substaion | transformer | major replacement | 862 | 1 | 19 | 79100 | LCN | 1 | 3
Array Cable | cable | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5

## OSW
Baseline case - offshore wind
Wind farm parameters
167 turbines
1 offshore substation
Export cable: 220 kV
Array cables: 66 kV
Wind turbine parameters
Capacity: 6 MW
Capex: $1,300/kW
power_curve: 2016CACost_NREL_Reference_6MW_155.csv |  | https://github.com/NREL/turbine-models/tree/master/Offshore
Maintenance inputs
annual service: 60 hours, CTV, $40,000
Failure and repair inputs
System | Subassembly Name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Severity Level
Turbine | electrical_system | minor repair | 2.414 | 1 | 5 | 226 | CTV | 0 | 1
Turbine | electrical_system | major repair | 54 | 1 | 14 | 4520 | CTV | 0 | 2
Turbine | electrical_system | major replacement | 432 | 1 | 18 | 27120 | CTV | 1 | 3
Turbine | electrical_system | relay minor repair | 2.725 | 1 | 4 | 588 | CTV | 0 | 1
Turbine | electrical_system | relay major repair | 16.45 | 1 | 19 | 5198 | CTV | 0 | 2
Turbine | electrical_system | relay major replacement | 444 | 1 | 150 | 30510 | CTV | 1 | 3
Turbine | electrical_system | power supply minor repair | 11.84 | 1 | 7 | 542 | CTV | 0 | 1
Turbine | electrical_system | power supply major repair | 11.1 | 1 | 14 | 11978 | CTV | 0 | 2
Turbine | electrical_system | power supply major replacement | 180 | 1 | 57 | 29380 | CTV | 1 | 3
Turbine | electronic_control | minor repair | 2.7 | 1 | 8 | 452 | CTV | 0 | 1
Turbine | electronic_control | major repair | 17.7 | 1 | 14 | 4520 | CTV | 0 | 2
Turbine | electronic_control | major replacement | 958 | 1 | 12 | 29380 | CTV | 1 | 3
Turbine | sensors | minor repair | 3.7 | 1 | 8 | 339 | CTV | 0 | 1
Turbine | sensors | major repair | 13.1 | 1 | 6 | 5650 | CTV | 0 | 2
Turbine | hydraulic_system | minor pitch system repair | 1.132 | 1 | 9 | 475 | CTV | 0 | 1
Turbine | hydraulic_system | major pitch system repair | 5.2 | 1 | 19 | 4294 | CTV | 0 | 2
Turbine | hydraulic_system | major pitch system replacement | 933 | 1 | 25 | 31640 | CTV | 1 | 3
Turbine | hydraulic_system | minor pump motor repair | 3.337 | 1 | 4 | 746 | CTV | 0 | 1
Turbine | hydraulic_system | major pump motor repair | 21.6 | 1 | 10 | 4520 | CTV | 0 | 2
Turbine | yaw_system | minor repair | 5.5 | 1 | 5 | 316 | CTV | 0 | 1
Turbine | yaw_system | major repair | 149 | 1 | 20 | 6780 | CTV | 0.3 | 2
Turbine | yaw_system | major replacement | 894 | 1 | 49 | 28250 | CTV | 1 | 3
Turbine | rotor_blades | minor repair | 1.969 | 1 | 9 | 384 | CTV | 0 | 1
Turbine | rotor_blades | major repair | 89.8 | 1 | 21 | 3390 | CTV | 0 | 2
Turbine | rotor_blades | major replacement | 898 | 1 | 288 | 203400 | LCN | 1 | 3
Turbine | mechanical_brake | other minor repair | 1.048 | 1 | 5 | 249 | CTV | 0 | 1
Turbine | mechanical_brake | other major repair | 20.3 | 1 | 21 | 5424 | CTV | 0 | 2
Turbine | mechanical_brake | other major replacement | 851 | 1 | 36 | 22600 | CTV | 0 | 3
Turbine | rotor_hub | n/a | 5.167 | 1 | 10 | 362 | CTV | 0 | 1
Turbine | rotor_hub | major repair | 24.7 | 1 | 40 | 3390 | CTV | 0 | 2
Turbine | rotor_hub | major replacement | 940 | 1 | 298 | 214700 | CTV | 1 | 3
Turbine | gearbox | minor repair | 2.348 | 1 | 8 | 283 | CTV | 0 | 1
Turbine | gearbox | major repair | 24.4 | 1 | 22 | 5650 | CTV | 0 | 2
Turbine | gearbox | major replacement | 6.022 | 1 | 231 | 519800 | LCN | 1 | 3
Turbine | generator | minor repair | 1.86 | 1 | 7 | 362 | CTV | 0 | 1
Turbine | generator | major repair | 2.8 | 1 | 24 | 7910 | CTV | 0 | 2
Turbine | generator | major replacement | 9.494 | 1 | 81 | 135600 | LCN | 1 | 3
Turbine | supporting_structure | minor repair | 10.6 | 1 | 5 | 316 | CTV | 0 | 1
Turbine | supporting_structure | major repair | 11 | 1 | 2 | 2486 | CTV | 0 | 2
Turbine | supporting_structure | minor safety repair | 2.578 | 1 | 2 | 294 | CTV | 0 | 1
Turbine | supporting_structure | major safety repair | 240 | 1 | 7 | 5424 | CTV | 0 | 2
Turbine | supporting_structure | minor service item repair | 8.1 | 1 | 7 | 181 | CTV | 0 | 1
Turbine | supporting_structure | major service item repair | 872 | 1 | 14 | 2712 | CTV | 0 | 2
Turbine | supporting_structure | minor HVAC repair | 4.868 | 1 | 5 | 1051 | CTV | 0 | 1
Turbine | supporting_structure | major HVAC repair | 132 | 1 | 14 | 2938 | CTV | 0 | 2
Turbine | drive_train | minor oil/grease repair | 2.154 | 1 | 4 | 362 | CTV | 0 | 1
Turbine | drive_train | major oil/grease repair | 146 | 1 | 18 | 4520 | CTV | 0 | 2
Substaion | transformer | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
Substaion | transformer | major repair | 287 | 1 | 26 | 2600 | CTV | 0 | 2
Substaion | transformer | major replacement | 862 | 1 | 19 | 79100 | LCN | 1 | 3
Array Cable | cable | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5

## LBW Results
Metric | Units | Project Total | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20
Time-based Availability | % | 44.2778 | 89.1145 | 78.3924 | 75.077 | 70.014 | 60.2481 | 55.2835 | 48.3601 | 44.9639 | 38.8873 | 32.5793 | 28.279 | 28.2917 | 30.9443 | 23.8969 | 21.8669 | 27.0364 | 30.917 | 34.8048 | 34.3999 | 32.236
Production-based Availability | % | 43.8629 | 89.4391 | 78.4405 | 75.1393 | 69.6966 | 60.4638 | 54.9925 | 47.8436 | 45.0798 | 38.7966 | 32.6221 | 28.0422 | 27.9599 | 30.7202 | 23.6717 | 21.6933 | 26.7797 | 30.6837 | 34.7349 | 34.4542 | 32.0695
Power Production | MW | 7793755.9235 | 768948.59 | 718328.0667 | 703222.597 | 584303.782 | 516742.422 | 461054.385 | 412613.699 | 361333.082 | 350039.453 | 257923.272 | 259673.741 | 249227.229 | 277752.105 | 229331.342 | 203494.031 | 241534.195 | 286864.654 | 298396.2894 | 315620.0614 | 297352.927
Net Capacity Factor | % | 21.6429 | 42.7359 | 39.9226 | 38.9762 | 32.4739 | 28.719 | 25.624 | 22.8692 | 20.0818 | ```````````````````````````` | 14.3346 | 14.3925 | 13.8513 | 15.4366 | 12.7456 | 11.2787 | 13.4238 | 15.9431 | 16.584 | 17.4933 | 16.526
Gross Capacity Factor | % | 49.3386 | 47.7821 | 50.8953 | 51.872 | 46.5932 | 47.4979 | 46.5955 | 47.8 | 44.5472 | 50.144 | 43.9415 | 51.3243 | 49.54 | 50.2491 | 53.8431 | 51.9917 | 50.1266 | 51.9594 | 47.7444 | 50.7726 | 51.5319
Task Completion Rate | % | 97.9013 | 85.8347 | 85.6899 | 98.3516 | 96.3203 | 93.5407 | 96.9388 | 101.4925 | 101.3333 | 105.4475 | 109.2105 | 111.4286 | 122.4359 | 98.1132 | 97.4843 | 101.4706 | 100 | 101.005 | 103.7815 | 98.4375 | 100.4484
Materials Cost | Millions USD$ | 35.1091 | 1.4472 | 1.5113 | 1.6442 | 2.032 | 1.7955 | 1.8728 | 2.096 | 2.2644 | 2.0831 | 2.2806 | 2.0993 | 2.0163 | 1.7106 | 1.3899 | 1.403 | 1.4732 | 1.4213 | 1.6988 | 1.3662 | 1.5035
Total Servicing Equipment Cost | Millions USD$ | 50.3475 | 2.3955 | 2.3821 | 2.6947 | 2.4529 | 2.4363 | 2.5196 | 2.7422 | 2.6754 | 2.3963 | 2.5813 | 2.573 | 2.5138 | 2.7163 | 2.4221 | 2.4372 | 2.4396 | 2.4729 | 2.6979 | 2.3622 | 2.4363
Cable Repair Truck Cost | Milllions USD$ | 3.512 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756 | 0.1756
Crawler Crane Cost | Milllions USD$ | 46.105 | 2.1833 | 2.17 | 2.4825 | 2.2408 | 2.2242 | 2.3075 | 2.53 | 2.4633 | 2.1842 | 2.3692 | 2.3608 | 2.3017 | 2.5042 | 2.21 | 2.225 | 2.2275 | 2.2608 | 2.4858 | 2.15 | 2.2242
Truck Cost | Milllions USD$ | 0.73053 | 0.036529 | 0.0365 | 0.0366 | 0.0365 | 0.0365 | 0.0365 | 0.0366 | 0.0365 | 0.0365 | 0.0365 | 0.0366 | 0.0365 | 0.0365 | 0.0365 | 0.0366 | 0.0365 | 0.0365 | 0.0365 | 0.0366 | 0.0365
Cable Repair Truck Utilization | % | 0.1612 | 0 | 0 | 0 | 3.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crawler Crane Utilization | % | 4.8515 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Truck Utilization | % | 4.9555 | 0 | 0 | 0 | 99.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0


## OSW Results
Metric | Units | Project Total | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20
Time-based Availability | % | 31.6125 | 89.8852 | 72.5387 | 57.8746 | 48.9333 | 41.5534 | 37.0599 | 31.2839 | 27.1356 | 23.7252 | 20.3547 | 18.9599 | 19.2883 | 19.7564 | 21.4474 | 21.0924 | 20.0198 | 18.0764 | 15.7154 | 14.0003 | 13.5893
Production-based Availability | % | 31.5615 | 90.224 | 72.8105 | 58.0531 | 48.8744 | 41.6395 | 37.1874 | 31.346 | 27.1228 | 23.7125 | 20.0949 | 18.8559 | 19.2267 | 19.7833 | 21.3715 | 21.0741 | 19.9575 | 17.9958 | 15.8309 | 13.9487 | 13.5517
Power Production | MW | 29321224.2386 | 3995338.458 | 3407374.424 | 2740495.7325 | 2204893.5106 | 2022783.325 | 1789939.074 | 1485203.3835 | 1250582.018 | 1143477.934 | 965937.864 | 829534.666 | 896405.228 | 960957.486 | 930260.397 | 897715.434 | 960718.376 | 821531.007 | 711154.52 | 656282.714 | 650638.687
Net Capacity Factor | % | 16.691 | 45.5179 | 38.8193 | 31.1364 | 25.1198 | 23.045 | 20.3923 | 16.8743 | 14.2476 | 13.0273 | 11.0047 | 9.4249 | 10.2125 | 10.9479 | 10.5982 | 10.1995 | 10.9452 | 9.3595 | 8.102 | 7.4564 | 7.4126
Gross Capacity Factor | % | 52.882 | 50.4498 | 53.3156 | 53.6344 | 51.3966 | 55.3442 | 54.8366 | 53.8324 | 52.5299 | 54.9388 | 54.7635 | 49.9836 | 53.1164 | 55.3393 | 49.5903 | 48.3982 | 54.8426 | 52.0093 | 51.1785 | 53.456 | 54.6984
Task Completion Rate | % | 96.4159 | 62.9398 | 68.8393 | 111.8727 | 130.2452 | 97.1108 | 95.6098 | 101.25 | 107.3604 | 105.949 | 110.9375 | 120.7407 | 114.8148 | 117.3913 | 97.0199 | 101.3793 | 101.1278 | 98.1343 | 98.8722 | 97.5 | 102.0202
Materials Cost | Millions USD$ | 85.125 | 3.4335 | 3.1129 | 2.7605 | 2.9915 | 4.4998 | 4.4427 | 5.3014 | 5.7408 | 5.3438 | 5.7348 | 6.2925 | 6.0897 | 5.1068 | 4.4892 | 3.8582 | 3.3982 | 3.6464 | 2.9765 | 3.2513 | 2.6544
Total Servicing Equipment Cost | Millions USD$ | 631.5049 | 28.4469 | 27.3433 | 25.9585 | 26.5092 | 35.0402 | 32.2997 | 33.0182 | 35.5597 | 33.1602 | 34.7443 | 34.3295 | 34.3689 | 34.186 | 36.1398 | 33.6149 | 33.8552 | 31.661 | 27.2208 | 28.216 | 25.8325
Cable Laying Vessel Cost | Milllions USD$ | 224.1 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205 | 11.205
Crew Transfer Vessel 1 Cost | Milllions USD$ | 12.7843 | 0.63926 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875
Crew Transfer Vessel 2 Cost | Milllions USD$ | 12.7843 | 0.63926 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875 | 0.63875 | 0.63875 | 0.6405 | 0.63875
Field Support Vessel Cost | Milllions USD$ | 3.458 | 0 | 0 | 0 | 0 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0.266 | 0 | 0 | 0
Heavy Lift Vessel Cost | Milllions USD$ | 89.375 | 0 | 0 | 0 | 0 | 8.125 | 5.0812 | 6.3563 | 8.4812 | 6.525 | 8.4125 | 8.2625 | 5.0563 | 6.1625 | 7.3812 | 7.4313 | 6.8 | 5.3 | 0 | 0 | 0
Jack-up Vessel Cost | Milllions USD$ | 289.0033 | 15.9633 | 14.8608 | 13.4725 | 14.0267 | 14.1667 | 14.47 | 13.91 | 14.33 | 13.8867 | 13.5833 | 13.315 | 16.5642 | 15.275 | 16.01 | 13.4317 | 14.3067 | 13.6125 | 14.7383 | 15.73 | 13.35
Cable Laying Vessel Utilization | % | 0.42988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3011 | 0 | 4.3011 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crew Transfer Vessel 1 Utilization | % | 6.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1366 | 0 | 57.8082 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crew Transfer Vessel 2 Utilization | % | 6.5845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1366 | 0 | 56.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Field Support Vessel Utilization | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heavy Lift Vessel Utilization | % | 7.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.1538 | 0 | 46.1538 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jack-up Vessel Utilization | % | 9.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6809 | 0 | 87.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0