## LBW
Baseline case - land-based wind
Wind farm parameters
79 turbines
1 substation
Array cables: 33 kV
Wind turbine parameters
Capacity: 2.6 MW
Capex: $850/kW
power_curve: 2019COE_Market_Average_2.6MW_121.csv |  | https://github.com/NREL/turbine-models/blob/master/Onshore/2019COE_Market_Average_2.6MW_121.csv
Maintenance inputs
annual service: 60 hours, CTV, $20,000
Failure and repair inputs
System | Subassembly Name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Severity Level
Turbine | electrical_system | minor repair | 2.414 | 1 | 5 | 113 | CTV | 0 | 1
Turbine | electrical_system | major repair | 54 | 1 | 14 | 2260 | CTV | 0 | 2
Turbine | electrical_system | major replacement | 432 | 1 | 18 | 14690 | CTV | 1 | 3
Turbine | electrical_system | relay minor repair | 2.725 | 1 | 4 | 294 | CTV | 0 | 1
Turbine | electrical_system | relay major repair | 16.45 | 1 | 19 | 2599 | CTV | 0 | 2
Turbine | electrical_system | relay major replacement | 444 | 1 | 150 | 15255 | CTV | 1 | 3
Turbine | electrical_system | power supply minor repair | 11.84 | 1 | 7 | 271 | CTV | 0 | 1
Turbine | electrical_system | power supply major repair | 11.1 | 1 | 14 | 5989 | CTV | 0 | 2
Turbine | electrical_system | power supply major replacement | 180 | 1 | 57 | 14690 | CTV | 1 | 3
Turbine | electronic_control | minor repair | 2.7 | 1 | 8 | 226 | CTV | 0 | 1
Turbine | electronic_control | major repair | 17.7 | 1 | 14 | 2260 | CTV | 0 | 2
Turbine | electronic_control | major replacement | 958 | 1 | 12 | 14690 | CTV | 1 | 3
Turbine | sensors | minor repair | 3.7 | 1 | 8 | 170 | CTV | 0 | 1
Turbine | sensors | major repair | 13.1 | 1 | 6 | 2825 | CTV | 0 | 2
Turbine | hydraulic_system | minor pitch system repair | 1.132 | 1 | 9 | 237 | CTV | 0 | 1
Turbine | hydraulic_system | major pitch system repair | 5.2 | 1 | 19 | 2147 | CTV | 0 | 2
Turbine | hydraulic_system | major pitch system replacement | 933 | 1 | 25 | 15820 | CTV | 1 | 3
Turbine | hydraulic_system | minor pump motor repair | 3.337 | 1 | 4 | 373 | CTV | 0 | 1
Turbine | hydraulic_system | major pump motor repair | 21.6 | 1 | 10 | 2260 | CTV | 0 | 2
Turbine | yaw_system | minor repair | 5.5 | 1 | 5 | 158 | CTV | 0 | 1
Turbine | yaw_system | major repair | 149 | 1 | 20 | 3390 | CTV | 0.3 | 2
Turbine | yaw_system | major replacement | 894 | 1 | 49 | 14125 | CTV | 1 | 3
Turbine | rotor_blades | minor repair | 1.969 | 1 | 9 | 192 | CTV | 0 | 1
Turbine | rotor_blades | major repair | 89.8 | 1 | 21 | 1695 | CTV | 0 | 2
Turbine | rotor_blades | major replacement | 898 | 1 | 288 | 101700 | LCN | 1 | 3
Turbine | mechanical_brake | other minor repair | 1.048 | 1 | 5 | 124 | CTV | 0 | 1
Turbine | mechanical_brake | other major repair | 20.3 | 1 | 21 | 2712 | CTV | 0 | 2
Turbine | mechanical_brake | other major replacement | 851 | 1 | 36 | 11300 | CTV | 0 | 3
Turbine | rotor_hub | n/a | 5.167 | 1 | 10 | 181 | CTV | 0 | 1
Turbine | rotor_hub | major repair | 24.7 | 1 | 40 | 1695 | CTV | 0 | 2
Turbine | rotor_hub | major replacement | 940 | 1 | 298 | 107350 | CTV | 1 | 3
Turbine | gearbox | minor repair | 2.348 | 1 | 8 | 141 | CTV | 0 | 1
Turbine | gearbox | major repair | 24.4 | 1 | 22 | 2825 | CTV | 0 | 2
Turbine | gearbox | major replacement | 6.022 | 1 | 231 | 259900 | LCN | 1 | 3
Turbine | generator | minor repair | 1.86 | 1 | 7 | 181 | CTV | 0 | 1
Turbine | generator | major repair | 2.8 | 1 | 24 | 3955 | CTV | 0 | 2
Turbine | generator | major replacement | 9.494 | 1 | 81 | 67800 | LCN | 1 | 3
Turbine | supporting_structure | minor repair | 10.6 | 1 | 5 | 158 | CTV | 0 | 1
Turbine | supporting_structure | major repair | 11 | 1 | 2 | 1243 | CTV | 0 | 2
Turbine | supporting_structure | minor safety repair | 2.578 | 1 | 2 | 147 | CTV | 0 | 1
Turbine | supporting_structure | major safety repair | 240 | 1 | 7 | 2712 | CTV | 0 | 2
Turbine | supporting_structure | minor service item repair | 8.1 | 1 | 7 | 90 | CTV | 0 | 1
Turbine | supporting_structure | major service item repair | 872 | 1 | 14 | 1356 | CTV | 0 | 2
Turbine | supporting_structure | minor HVAC repair | 4.868 | 1 | 5 | 525 | CTV | 0 | 1
Turbine | supporting_structure | major HVAC repair | 132 | 1 | 14 | 1469 | CTV | 0 | 2
Turbine | drive_train | minor oil/grease repair | 2.154 | 1 | 4 | 181 | CTV | 0 | 1
Turbine | drive_train | major oil/grease repair | 146 | 1 | 18 | 2260 | CTV | 0 | 2
Substaion | transformer | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
Substaion | transformer | major repair | 287 | 1 | 26 | 2599 | CTV | 0 | 2
Substaion | transformer | major replacement | 862 | 1 | 19 | 79100 | LCN | 1 | 3
Array Cable | cable | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5

## OSW
Baseline case - offshore wind
Wind farm parameters
167 turbines
1 offshore substation
Export cable: 220 kV
Array cables: 66 kV
Wind turbine parameters
Capacity: 6 MW
Capex: $1,300/kW
power_curve: 2016CACost_NREL_Reference_6MW_155.csv |  | https://github.com/NREL/turbine-models/tree/master/Offshore
Maintenance inputs
annual service: 60 hours, CTV, $40,000
Failure and repair inputs
System | Subassembly Name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Severity Level
Turbine | electrical_system | minor repair | 2.414 | 1 | 5 | 226 | CTV | 0 | 1
Turbine | electrical_system | major repair | 54 | 1 | 14 | 4520 | CTV | 0 | 2
Turbine | electrical_system | major replacement | 432 | 1 | 18 | 27120 | CTV | 1 | 3
Turbine | electrical_system | relay minor repair | 2.725 | 1 | 4 | 588 | CTV | 0 | 1
Turbine | electrical_system | relay major repair | 16.45 | 1 | 19 | 5198 | CTV | 0 | 2
Turbine | electrical_system | relay major replacement | 444 | 1 | 150 | 30510 | CTV | 1 | 3
Turbine | electrical_system | power supply minor repair | 11.84 | 1 | 7 | 542 | CTV | 0 | 1
Turbine | electrical_system | power supply major repair | 11.1 | 1 | 14 | 11978 | CTV | 0 | 2
Turbine | electrical_system | power supply major replacement | 180 | 1 | 57 | 29380 | CTV | 1 | 3
Turbine | electronic_control | minor repair | 2.7 | 1 | 8 | 452 | CTV | 0 | 1
Turbine | electronic_control | major repair | 17.7 | 1 | 14 | 4520 | CTV | 0 | 2
Turbine | electronic_control | major replacement | 958 | 1 | 12 | 29380 | CTV | 1 | 3
Turbine | sensors | minor repair | 3.7 | 1 | 8 | 339 | CTV | 0 | 1
Turbine | sensors | major repair | 13.1 | 1 | 6 | 5650 | CTV | 0 | 2
Turbine | hydraulic_system | minor pitch system repair | 1.132 | 1 | 9 | 475 | CTV | 0 | 1
Turbine | hydraulic_system | major pitch system repair | 5.2 | 1 | 19 | 4294 | CTV | 0 | 2
Turbine | hydraulic_system | major pitch system replacement | 933 | 1 | 25 | 31640 | CTV | 1 | 3
Turbine | hydraulic_system | minor pump motor repair | 3.337 | 1 | 4 | 746 | CTV | 0 | 1
Turbine | hydraulic_system | major pump motor repair | 21.6 | 1 | 10 | 4520 | CTV | 0 | 2
Turbine | yaw_system | minor repair | 5.5 | 1 | 5 | 316 | CTV | 0 | 1
Turbine | yaw_system | major repair | 149 | 1 | 20 | 6780 | CTV | 0.3 | 2
Turbine | yaw_system | major replacement | 894 | 1 | 49 | 28250 | CTV | 1 | 3
Turbine | rotor_blades | minor repair | 1.969 | 1 | 9 | 384 | CTV | 0 | 1
Turbine | rotor_blades | major repair | 89.8 | 1 | 21 | 3390 | CTV | 0 | 2
Turbine | rotor_blades | major replacement | 898 | 1 | 288 | 203400 | LCN | 1 | 3
Turbine | mechanical_brake | other minor repair | 1.048 | 1 | 5 | 249 | CTV | 0 | 1
Turbine | mechanical_brake | other major repair | 20.3 | 1 | 21 | 5424 | CTV | 0 | 2
Turbine | mechanical_brake | other major replacement | 851 | 1 | 36 | 22600 | CTV | 0 | 3
Turbine | rotor_hub | n/a | 5.167 | 1 | 10 | 362 | CTV | 0 | 1
Turbine | rotor_hub | major repair | 24.7 | 1 | 40 | 3390 | CTV | 0 | 2
Turbine | rotor_hub | major replacement | 940 | 1 | 298 | 214700 | CTV | 1 | 3
Turbine | gearbox | minor repair | 2.348 | 1 | 8 | 283 | CTV | 0 | 1
Turbine | gearbox | major repair | 24.4 | 1 | 22 | 5650 | CTV | 0 | 2
Turbine | gearbox | major replacement | 6.022 | 1 | 231 | 519800 | LCN | 1 | 3
Turbine | generator | minor repair | 1.86 | 1 | 7 | 362 | CTV | 0 | 1
Turbine | generator | major repair | 2.8 | 1 | 24 | 7910 | CTV | 0 | 2
Turbine | generator | major replacement | 9.494 | 1 | 81 | 135600 | LCN | 1 | 3
Turbine | supporting_structure | minor repair | 10.6 | 1 | 5 | 316 | CTV | 0 | 1
Turbine | supporting_structure | major repair | 11 | 1 | 2 | 2486 | CTV | 0 | 2
Turbine | supporting_structure | minor safety repair | 2.578 | 1 | 2 | 294 | CTV | 0 | 1
Turbine | supporting_structure | major safety repair | 240 | 1 | 7 | 5424 | CTV | 0 | 2
Turbine | supporting_structure | minor service item repair | 8.1 | 1 | 7 | 181 | CTV | 0 | 1
Turbine | supporting_structure | major service item repair | 872 | 1 | 14 | 2712 | CTV | 0 | 2
Turbine | supporting_structure | minor HVAC repair | 4.868 | 1 | 5 | 1051 | CTV | 0 | 1
Turbine | supporting_structure | major HVAC repair | 132 | 1 | 14 | 2938 | CTV | 0 | 2
Turbine | drive_train | minor oil/grease repair | 2.154 | 1 | 4 | 362 | CTV | 0 | 1
Turbine | drive_train | major oil/grease repair | 146 | 1 | 18 | 4520 | CTV | 0 | 2
Substaion | transformer | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
Substaion | transformer | major repair | 287 | 1 | 26 | 2600 | CTV | 0 | 2
Substaion | transformer | major replacement | 862 | 1 | 19 | 79100 | LCN | 1 | 3
Array Cable | cable | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5

## LBW Results
Metric | Units | Project Total | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20
Time-based Availability | % | 38.9335 | 90.8836 | 72.2356 | 61.2897 | 49.6364 | 39.4493 | 32.969 | 32.8048 | 33.1676 | 33.7704 | 34.7669 | 33.3002 | 31.5139 | 31.2054 | 30.882 | 29.1906 | 27.7913 | 29.049 | 28.493 | 27.2359 | 29.0644
Production-based Availability | % | 38.8065 | 91.1482 | 72.821 | 61.4123 | 49.5519 | 39.5647 | 32.8428 | 32.5778 | 33.0368 | 33.7477 | 34.8174 | 32.9972 | 31.2876 | 31.0245 | 30.6007 | 29.2512 | 27.6717 | 28.8939 | 28.3849 | 27.1784 | 28.8257
Power Production | MW | 6895299.0736 | 783643.154 | 666866.588 | 574752.7457 | 415420.142 | 338132.1765 | 275352.309 | 280958.7784 | 264803.671 | 304486.851 | 275280.764 | 305557.272 | 278889.459 | 280502.92 | 296459.494 | 274391.726 | 249578.87 | 270131.186 | 243844.913 | 248969.682 | 267276.372
Net Capacity Factor | % | 19.1479 | 43.5526 | 37.0625 | 31.8558 | 23.0878 | 18.7924 | 15.3033 | 15.5722 | 14.717 | 16.9225 | 15.2993 | 16.9356 | 15.4999 | 15.5895 | 16.4763 | 15.2082 | 13.8709 | 15.0131 | 13.5522 | 13.7992 | 14.8544
Gross Capacity Factor | % | 49.3386 | 47.7821 | 50.8953 | 51.872 | 46.5932 | 47.4979 | 46.5955 | 47.8 | 44.5472 | 50.144 | 43.9415 | 51.3243 | 49.54 | 50.2491 | 53.8431 | 51.9917 | 50.1266 | 51.9594 | 47.7444 | 50.7726 | 51.5319
Task Completion Rate | % | 98.1933 | 83.4951 | 98.4674 | 92.8251 | 94.8485 | 102.3649 | 110.4803 | 110.8597 | 105.2632 | 100 | 99.6063 | 99.5833 | 99.1803 | 101.4706 | 98.6667 | 99.4652 | 100.5128 | 100 | 98.0392 | 100 | 102.2472
Materials Cost | USD$/kW | 167.605 | 7.3387 | 7.8033 | 8.8128 | 8.1477 | 10.6028 | 10.8025 | 10.9673 | 8.3336 | 9.1707 | 9.0651 | 7.6975 | 7.6813 | 7.7168 | 7.6116 | 7.4647 | 7.7642 | 7.6125 | 9.2518 | 7.1172 | 6.6429
Total Servicing Equipment Cost | USD$/kW | 246.2798 | 12.3319 | 12.7577 | 12.4458 | 11.6501 | 12.4331 | 12.2668 | 12.6527 | 11.7678 | 12.8632 | 13.3419 | 11.9468 | 11.6663 | 11.9544 | 12.5427 | 11.8656 | 12.4494 | 12.7537 | 12.352 | 12.2795 | 11.9585
Cable Repair Truck Cost | USD$/kW | 17.0983 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492 | 0.85492
Crawler Crane Cost | USD$/kW | 225.6248 | 11.2991 | 11.7251 | 11.4127 | 10.6175 | 11.4005 | 11.2342 | 11.6196 | 10.7352 | 11.8306 | 12.3093 | 10.9137 | 10.6337 | 10.9218 | 11.5101 | 10.8325 | 11.4167 | 11.721 | 11.3194 | 11.2463 | 10.9258
Truck Cost | USD$/kW | 3.5566 | 0.17784 | 0.1777 | 0.17819 | 0.1777 | 0.1777 | 0.1777 | 0.17819 | 0.1777 | 0.1777 | 0.1777 | 0.17819 | 0.1777 | 0.1777 | 0.1777 | 0.17819 | 0.1777 | 0.1777 | 0.1777 | 0.17819 | 0.1777
Cable Repair Truck Utilization | % | 0.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2258 | 0 | 0
Crawler Crane Utilization | % | 5.0197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
Truck Utilization | % | 3.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.8219 | 0 | 0

## OSW Results
Metric | Units | Project Total | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20
Time-based Availability | % | 30.1946 | 87.8435 | 67.0815 | 55.366 | 44.1506 | 36.653 | 33.0276 | 31.5934 | 29.6893 | 25.4514 | 22.682 | 22.4567 | 21.9362 | 19.3861 | 17.6026 | 15.0998 | 14.8549 | 14.6907 | 14.9815 | 14.2948 | 15.0827
Production-based Availability | % | 30.2073 | 88.1698 | 67.4555 | 55.6368 | 44.1846 | 36.8351 | 33.0942 | 31.5976 | 29.5896 | 25.4888 | 22.7798 | 22.3367 | 21.8353 | 19.44 | 17.6648 | 15.1425 | 14.7413 | 14.6914 | 15.049 | 14.2947 | 15.1332
Power Production | MW | 28063182.1325 | 3904372.6006 | 3156771.9614 | 2626427.1843 | 1993319.145 | 1789394.2699 | 1592921.275 | 1497125.885 | 1364321.836 | 1229138.344 | 1094994.21 | 982668.657 | 1018028.199 | 944282.2263 | 768912.28 | 645039.562 | 709620.922 | 670681.05 | 676030.64 | 672563.106 | 726568.779
Net Capacity Factor | % | 15.9749 | 44.4815 | 35.9643 | 29.8404 | 22.7094 | 20.3861 | 18.1477 | 17.0098 | 15.5434 | 14.0033 | 12.475 | 11.1647 | 11.5981 | 10.758 | 8.76 | 7.3287 | 8.0845 | 7.6409 | 7.7018 | 7.6414 | 8.2776
Gross Capacity Factor | % | 52.882 | 50.4498 | 53.3156 | 53.6344 | 51.3966 | 55.3442 | 54.8366 | 53.8324 | 52.5299 | 54.9388 | 54.7635 | 49.9836 | 53.1164 | 55.3393 | 49.5903 | 48.3982 | 54.8426 | 52.0093 | 51.1785 | 53.456 | 54.6984
Task Completion Rate | % | 96.4575 | 60.8661 | 67.5926 | 97.3934 | 143.4251 | 116.5049 | 100 | 102.3305 | 102.3529 | 104.7619 | 108 | 109.5385 | 109.7179 | 119.9288 | 98.227 | 97.7974 | 100.4545 | 101.0309 | 97.9487 | 101.8868 | 98.9899
Materials Cost | USD$/kW | 86.7032 | 3.3396 | 3.3697 | 3.0979 | 3.3128 | 4.4911 | 4.9953 | 5.562 | 5.6074 | 5.4963 | 5.8644 | 5.647 | 5.6964 | 5.8456 | 3.8821 | 3.973 | 3.2366 | 4.0142 | 3.0261 | 3.1582 | 3.0871
Total Servicing Equipment Cost | USD$/kW | 643.8309 | 27.1733 | 28.4298 | 26.9779 | 28.4298 | 33.966 | 35.7799 | 31.6799 | 35.4888 | 34.3282 | 35.4859 | 34.6103 | 34.6184 | 35.853 | 33.9094 | 34.3978 | 33.7992 | 35.6248 | 27.0093 | 28.1597 | 28.1096
Cable Laying Vessel Cost | USD$/kW | 223.6527 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826 | 11.1826
Crew Transfer Vessel 1 Cost | USD$/kW | 12.7587 | 0.63798 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748
Crew Transfer Vessel 2 Cost | USD$/kW | 12.7587 | 0.63798 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748 | 0.63748 | 0.63748 | 0.63922 | 0.63748
Field Support Vessel Cost | USD$/kW | 3.4511 | 0 | 0 | 0 | 0 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0.26547 | 0 | 0 | 0
Heavy Lift Vessel Cost | USD$/kW | 89.8765 | 0 | 0 | 0 | 0 | 7.1045 | 7.6784 | 5.0711 | 8.4643 | 6.512 | 6.8488 | 8.5953 | 5.3643 | 6.5931 | 5.121 | 7.4164 | 6.7864 | 8.3209 | 0 | 0 | 0
Jack-up Vessel Cost | USD$/kW | 301.3332 | 14.7147 | 15.9722 | 14.5168 | 15.9722 | 14.1384 | 15.3784 | 13.8822 | 14.3014 | 15.0931 | 15.914 | 13.2884 | 16.5311 | 16.5369 | 16.0654 | 14.2548 | 14.2898 | 14.5808 | 14.5517 | 15.6986 | 15.652
Cable Laying Vessel Utilization | % | 0.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crew Transfer Vessel 1 Utilization | % | 3.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crew Transfer Vessel 2 Utilization | % | 3.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Field Support Vessel Utilization | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heavy Lift Vessel Utilization | % | 2.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 41.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jack-up Vessel Utilization | % | 4.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0