## LBW
Baseline case - land-based wind
Wind farm parameters
79 turbines
1 substation
Array cables: 33 kV
Wind turbine parameters
Capacity: 2.6 MW
Capex: $850/kW
power_curve: 2019COE_Market_Average_2.6MW_121.csv |  | https://github.com/NREL/turbine-models/blob/master/Onshore/2019COE_Market_Average_2.6MW_121.csv
Maintenance inputs
annual service: 60 hours, CTV, $20,000
Failure and repair inputs
System | Subassembly Name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Severity Level
Turbine | electrical_system | minor repair | 2.414 | 1 | 5 | 113 | CTV | 0 | 1
electrical_system |  | major repair | 54 | 1 | 14 | 2260 | CTV | 0 | 2
electrical_system |  | major replacement | 432 | 1 | 18 | 14690 | CTV | 1 | 3
electrical_system |  | relay minor repair | 2.725 | 1 | 4 | 294 | CTV | 0 | 1
electrical_system |  | relay major repair | 16.45 | 1 | 19 | 2599 | CTV | 0 | 2
electrical_system |  | relay major replacement | 444 | 1 | 150 | 15255 | CTV | 1 | 3
electrical_system |  | power supply minor repair | 11.84 | 1 | 7 | 271 | CTV | 0 | 1
electrical_system |  | power supply major repair | 11.1 | 1 | 14 | 5989 | CTV | 0 | 2
electrical_system |  | power supply major replacement | 180 | 1 | 57 | 14690 | CTV | 1 | 3
electronic_control |  | minor repair | 2.7 | 1 | 8 | 226 | CTV | 0 | 1
electronic_control |  | major repair | 17.7 | 1 | 14 | 2260 | CTV | 0 | 2
electronic_control |  | major replacement | 958 | 1 | 12 | 14690 | CTV | 1 | 3
sensors |  | minor repair | 3.7 | 1 | 8 | 170 | CTV | 0 | 1
sensors |  | major repair | 13.1 | 1 | 6 | 2825 | CTV | 0 | 2
hydraulic_system |  | minor pitch system repair | 1.132 | 1 | 9 | 237 | CTV | 0 | 1
hydraulic_system |  | major pitch system repair | 5.2 | 1 | 19 | 2147 | CTV | 0 | 2
hydraulic_system |  | major pitch system replacement | 933 | 1 | 25 | 15820 | CTV | 1 | 3
hydraulic_system |  | minor pump motor repair | 3.337 | 1 | 4 | 373 | CTV | 0 | 1
hydraulic_system |  | major pump motor repair | 21.6 | 1 | 10 | 2260 | CTV | 0 | 2
yaw_system |  | minor repair | 5.5 | 1 | 5 | 158 | CTV | 0 | 1
yaw_system |  | major repair | 149 | 1 | 20 | 3390 | CTV | 0.3 | 2
yaw_system |  | major replacement | 894 | 1 | 49 | 14125 | CTV | 1 | 3
rotor_blades |  | minor repair | 1.969 | 1 | 9 | 192 | CTV | 0 | 1
rotor_blades |  | major repair | 89.8 | 1 | 21 | 1695 | CTV | 0 | 2
rotor_blades |  | major replacement | 898 | 1 | 288 | 101700 | CRN | 1 | 3
mechanical_brake |  | other minor repair | 1.048 | 1 | 5 | 124 | CTV | 0 | 1
mechanical_brake |  | other major repair | 20.3 | 1 | 21 | 2712 | CTV | 0 | 2
mechanical_brake |  | other major replacement | 851 | 1 | 36 | 11300 | CTV | 0 | 3
rotor_hub |  | minor repair | 5.167 | 1 | 10 | 181 | CTV | 0 | 1
rotor_hub |  | major repair | 24.7 | 1 | 40 | 1695 | CTV | 0 | 2
rotor_hub |  | major replacement | 940 | 1 | 298 | 107350 | CTV | 1 | 3
gearbox |  | minor repair | 2.348 | 1 | 8 | 141 | CTV | 0 | 1
gearbox |  | major repair | 24.4 | 1 | 22 | 2825 | CTV | 0 | 2
gearbox |  | major replacement | 6.022 | 1 | 231 | 259900 | CRN | 1 | 3
generator |  | minor repair | 1.86 | 1 | 7 | 181 | CTV | 0 | 1
generator |  | major repair | 2.8 | 1 | 24 | 3955 | CTV | 0 | 2
generator |  | major replacement | 9.494 | 1 | 81 | 67800 | CRN | 1 | 3
supporting_structure |  | minor repair | 10.6 | 1 | 5 | 158 | CTV | 0 | 1
supporting_structure |  | major repair | 11 | 1 | 2 | 1243 | CTV | 0 | 2
supporting_structure |  | minor safety repair | 2.578 | 1 | 2 | 147 | CTV | 0 | 1
supporting_structure |  | major safety repair | 240 | 1 | 7 | 2712 | CTV | 0 | 2
supporting_structure |  | minor service item repair | 8.1 | 1 | 7 | 90 | CTV | 0 | 1
supporting_structure |  | major service item repair | 872 | 1 | 14 | 1356 | CTV | 0 | 2
supporting_structure |  | minor HVAC repair | 4.868 | 1 | 5 | 525 | CTV | 0 | 1
supporting_structure |  | major HVAC repair | 132 | 1 | 14 | 1469 | CTV | 0 | 2
drive_train |  | minor oil/grease repair | 2.154 | 1 | 4 | 181 | CTV | 0 | 1
drive_train |  | major oil/grease repair | 146 | 1 | 18 | 2260 | CTV | 0 | 2
OSS_transformer |  | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
OSS_transformer |  | major repair | 287 | 1 | 26 | 2600 | CTV | 0 | 2
OSS_transformer |  | major replacement | 862 | 1 | 19 | 79100 | CRN | 1 | 3
array_cable |  | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5

## OSW
Baseline case - offshore wind
Wind farm parameters
167 turbines
1 offshore substation
Export cable: 220 kV
Array cables: 66 kV
Wind turbine parameters
Capacity: 6 MW
Capex: $1,300/kW
power_curve: 2016CACost_NREL_Reference_6MW_155.csv |  | https://github.com/NREL/turbine-models/tree/master/Offshore
Maintenance inputs
annual service: 60 hours, CTV, $40,000
Failure and repair inputs
System name | Description | Weibull scale | Weibull shape | Time (h) | Materials cost ($) | Service equipment | Operation reduction | Level
electrical_system | minor repair | 2.414 | 1 | 5 | 226 | CTV | 0 | 1
electrical_system | major repair | 54 | 1 | 14 | 4520 | CTV | 0 | 2
electrical_system | major replacement | 432 | 1 | 18 | 27120 | CTV | 1 | 3
electrical_system | relay minor repair | 2.725 | 1 | 4 | 588 | CTV | 0 | 1
electrical_system | relay major repair | 16.45 | 1 | 19 | 5198 | CTV | 0 | 2
electrical_system | relay major replacement | 444 | 1 | 150 | 30510 | CTV | 1 | 3
electrical_system | power supply minor repair | 11.84 | 1 | 7 | 542 | CTV | 0 | 1
electrical_system | power supply major repair | 11.1 | 1 | 14 | 11978 | CTV | 0 | 2
electrical_system | power supply major replacement | 180 | 1 | 57 | 29380 | CTV | 1 | 3
electronic_control | minor repair | 2.7 | 1 | 8 | 452 | CTV | 0 | 1
electronic_control | major repair | 17.7 | 1 | 14 | 4520 | CTV | 0 | 2
electronic_control | major replacement | 958 | 1 | 12 | 29380 | CTV | 1 | 3
sensors | minor repair | 3.7 | 1 | 8 | 339 | CTV | 0 | 1
sensors | major repair | 13.1 | 1 | 6 | 5650 | CTV | 0 | 2
hydraulic_system | minor pitch system repair | 1.132 | 1 | 9 | 475 | CTV | 0 | 1
hydraulic_system | major pitch system repair | 5.2 | 1 | 19 | 4294 | CTV | 0 | 2
hydraulic_system | major pitch system replacement | 933 | 1 | 25 | 31640 | CTV | 1 | 3
hydraulic_system | minor pump motor repair | 3.337 | 1 | 4 | 746 | CTV | 0 | 1
hydraulic_system | major pump motor repair | 21.6 | 1 | 10 | 4520 | CTV | 0 | 2
yaw_system | minor repair | 5.5 | 1 | 5 | 316 | CTV | 0 | 1
yaw_system | major repair | 149 | 1 | 20 | 6780 | CTV | 0.3 | 2
yaw_system | major replacement | 894 | 1 | 49 | 28250 | CTV | 1 | 3
rotor_blades | minor repair | 1.969 | 1 | 9 | 384 | CTV | 0 | 1
rotor_blades | major repair | 89.8 | 1 | 21 | 3390 | CTV | 0 | 2
rotor_blades | major replacement | 898 | 1 | 288 | 203400 | WTIV | 1 | 3
mechanical_brake | other minor repair | 1.048 | 1 | 5 | 249 | CTV | 0 | 1
mechanical_brake | other major repair | 20.3 | 1 | 21 | 5424 | CTV | 0 | 2
mechanical_brake | other major replacement | 851 | 1 | 36 | 22600 | CTV | 0 | 3
rotor_hub | minor repair | 5.167 | 1 | 10 | 362 | CTV | 0 | 1
rotor_hub | major repair | 24.7 | 1 | 40 | 3390 | CTV | 0 | 2
rotor_hub | major replacement | 940 | 1 | 298 | 214700 | CTV | 1 | 3
gearbox | minor repair | 2.348 | 1 | 8 | 283 | CTV | 0 | 1
gearbox | major repair | 24.4 | 1 | 22 | 5650 | CTV | 0 | 2
gearbox | major replacement | 6.022 | 1 | 231 | 519800 | WTIV | 1 | 3
generator | minor repair | 1.86 | 1 | 7 | 362 | CTV | 0 | 1
generator | major repair | 2.8 | 1 | 24 | 7910 | CTV | 0 | 2
generator | major replacement | 9.494 | 1 | 81 | 135600 | WTIV | 1 | 3
supporting_structure | minor repair | 10.6 | 1 | 5 | 316 | CTV | 0 | 1
supporting_structure | major repair | 11 | 1 | 2 | 2486 | CTV | 0 | 2
supporting_structure | minor safety repair | 2.578 | 1 | 2 | 294 | CTV | 0 | 1
supporting_structure | major safety repair | 240 | 1 | 7 | 5424 | CTV | 0 | 2
supporting_structure | minor service item repair | 8.1 | 1 | 7 | 181 | CTV | 0 | 1
supporting_structure | major service item repair | 872 | 1 | 14 | 2712 | CTV | 0 | 2
supporting_structure | minor HVAC repair | 4.868 | 1 | 5 | 1051 | CTV | 0 | 1
supporting_structure | major HVAC repair | 132 | 1 | 14 | 2938 | CTV | 0 | 2
drive_train | minor oil/grease repair | 2.154 | 1 | 4 | 362 | CTV | 0 | 1
drive_train | major oil/grease repair | 146 | 1 | 18 | 4520 | CTV | 0 | 2
OSS_transformer | minor repair | 16.568 | 1 | 7 | 107 | CTV | 0 | 1
OSS_transformer | major repair | 287 | 1 | 26 | 2600 | CTV | 0 | 2
OSS_transformer | major replacement | 862 | 1 | 19 | 79100 | HLV | 1 | 3
array_cable | cable replacement | 2500 | 1 | 32 | 350000 | CAB | 1 | 5